## 2360-190602
| Survey No | INIS-110819-620 |  | Item Surveyed |  | FE-2 Fan and Duct
| Date | 2019-11-07 |  | Comments
| Survey Tech | A. Peden/R. Florence
| Count Room Tech | N/A |  | Parameters |  | Gamma |  |  | Total Activity |  |  |  | Removable Activity |  |  |  | 1.4142
| Date Counted | N/A |  |  |  | CPM | µR/hr | µRem/hr | Alpha |  | Beta-Gamma |  | Alpha |  | Beta-Gamma |  | 0
| Survey Type | Characterization |  |  | Instrument Model | 2221 |  |  | 2360/43-93 |  | 2360/43-93 | [5 empty] | 0
| Level of Posting | None |  |  | Instrument SN | 172045 |  |  | 227431/PR289429 |  | 227431/PR289429 | [5 empty] | 1.4142
Notes |  |  | Total Activity |  | Cal. Due Date | 2020-06-13 |  |  | 2020-08-12 |  | 2020-08-12 | [5 empty] | 17.1464
PCF = Probe Correction Factor |  |  | dpm = (cpm - Bcpm)/(eff * PCF) |  | Efficiency |  |  |  | 22.18% |  | 37.05% | [5 empty] | 24.2487
Tb = Background count time |  |  | Removable Activity |  | Background Counts | 5600 |  |  | 0 |  | 294
Ts = Sample count time |  |  | dpm = (cpm - Bcpm)/ eff |  | PCF |  |  |  | 1 |  | 1
Rb = Background count rate |  |  | *dpm results are per 100cm2 |  | Tb |  |  |  | 1 |  | 1
Bcpm = Background cpm |  |  |  |  | Ts |  |  |  | 1 |  | 1
MDCR = Minimum Detectable Count Rate (net cpm) |  |  |  | MDCR |  |  |  |  | 3 |  | 82.7783
MDC = Minimum Detectable Concentration (dpm per 100cm2) |  |  |  | MDC |  |  |  |  | 13.5257 |  | 223.4231
No. | Descriptions |  |  |  |  | cpm | µR/hr | µRem/hr | gross counts | *dpm | gross counts | *dpm | gross counts | *dpm | gross counts | *dpm
1 | FE-2 housing bottom north side |  |  |  |  | 7471 |  |  | 0 | 0 | 280 | -37.7868
2 | FE-2 housing side north side |  |  |  |  | 6591 |  |  | 2 | 9.0171 | 288 | -16.1943
3 | FE-2 duct top north side |  |  |  |  | 6689 |  |  | 2 | 9.0171 | 306 | 32.3887
4 | FE-2 exhaust duct west side |  |  |  |  | 5206 |  |  | 0 | 0 | 248 | -124.1565
5 | FE-2 housing front west side |  |  |  |  | 7028 |  |  | 0 | 0 | 292 | -5.3981
6 | FE-2 housing bottom south side |  |  |  |  | 8139 |  |  | 0 | 0 | 387 | 251.0121
7 | FE-2 housing side south side |  |  |  |  | 7621 |  |  | 0 | 0 | 340 | 124.1565
8 | FE-2 housing top south side |  |  |  |  | 7820 |  |  | 2 | 9.0171 | 347 | 143.0499
9 | FE-2 exhaust duct noth side |  |  |  |  | 5739 |  |  | 0 | 0 | 312 | 48.583
10 | FE-2 exhaust duct overhead bottom |  |  |  |  | 5387 |  |  | 4 | 18.0343 | 258 | -97.166
11 | FE-2 exhaust duct west side overhed |  |  |  |  | 4870 |  |  | 0 | 0 | 258 | -97.166
12 | FE-2 exhaust duct bottom overhed |  |  |  |  | 5486 |  |  | 0 | 0 | 358 | 172.7395
13 | FE-2 exhaust duct bottom overhed |  |  |  |  | 5232 |  |  | 2 | 9.0171 | 394 | 269.9055
14 | FE-2 exhaust duct west side overhed |  |  |  |  | 4912 |  |  | 0 | 0 | 292 | -5.3981
15 | FE-2 exhaust duct bottom overhed |  |  |  |  | 4952 |  |  | 0 | 0 | 218 | -205.1282
16 | FE-2 exhaust duct west side overhed |  |  |  |  | 5470 |  |  | 4 | 18.0343 | 322 | 75.5735
17 | FE-2 exhaust duct east side overhed |  |  |  |  | 5337 |  |  | 0 | 0 | 324 | 80.9717
18 | FE-2 exhaust duct east side overhed |  |  |  |  | 5451 |  |  | 0 | 0 | 286 | -21.5924
19 | FE-2 exhaust duct east side overhed |  |  |  |  | 5528 |  |  | 0 | 0 | 314 | 53.9811

## Map
Survey No | INIS-110819-620
Date | 2019-11-07
Survey Tech | A. Peden/R. Florence
Count Room Tech | N/A
Date Counted | N/A
Survey Type | Characterization
Level of Posting | None
Comments

## Map (2)
Survey No | INIS-110719-620
Date | 2019-11-07
Survey Tech | A. Peden/R. Florence
Count Room Tech | N/A
Date Counted | N/A
Survey Type | Characterization
Level of Posting | None
Comments

## Map (3)
Survey No | INIS-110719-620
Date | 2019-11-07
Survey Tech | A. Peden/R. Florence
Count Room Tech | N/A
Date Counted | N/A
Survey Type | Characterization
Level of Posting | None
Comments

## Map (4)
Survey No | INIS-110719-620
Date | 2019-11-07
Survey Tech | A. Peden/R. Florence
Count Room Tech | N/A
Date Counted | N/A
Survey Type | Characterization
Level of Posting | None
Comments